New conductor types application for overhead transmission lines design optimization and reliability improvement

L. TIMASHOVA, E. NIKIFOROV, I. NAZAROV, A. MERZLYAKOV

«R&D Center @ FGS», JSC

M. ERMOSHINA L. KACHANOVSKAYA, E. KONSTANTINOVA, P. ROMANOV

«North-West Power Engineering Center», JSC

S. KOLOSOV*                     V. SHKAPTSOV

«Electrosetstroyproekt», JSC               GC OPTEN

Russia

SUMMARY

Growth of electrical energy consumption increases the urgent interest to improve capacity and reliability of overhead transmission lines. This leads to the need to develop and apply new design and construction solutions, to use modern materials and technologies. Application of new materials and optimized design solutions is also necessary on the way of wide-scale renovation of the network infrastructure with lifetime more than 40-50 years. Social and economical conditions of this renovation suggest rational and effective solutions on the basis of feasibility mapping.

Analysis of international and domestic progressive experience shows that when constructing a new OHL and renovating existing OHL it is advisable to use new generation conductors with improved mechanical and electrical properties compared to traditional ACSR conductors. This report presents the experience of practical application and development of a new generation of conductors. Electrical and mechanical characteristics of these conductors make possible to achieve such positive effects as increased reliability and transmitting capacity of OHL, guaranteed security distance between conductors and ground or intersected objects. Application of new generation conductors preserving mechanical properties in conditions of prolonged operation at high temperatures is particularly effective in complex emergency and post-emergency conditions of the network, when required flows of energy and power are transmitted through remaining in operation N-1, N-2 lines. Series of tests were carried out to determine new conductors’ mechanical and electrical parameters.. Data on mechanical and electrical characteristics of new conductors, obtained during the research, allows to execute a number of promising projects of OHL renovation.

In this report a successful practical experience of application in Russian network utilities of ACCR conductors, developed and manufactured by 3M Company (USA); conductors GTACSR manufactured by company J-Power (Japan), ACCC conductors with the CTC’s composite core produced by LAMIFIL (Belgium) is presented.

Test results of Russian compacted HTLS conductor with high strength carbon composite core (which is an analogue of ACCC conductor) are as well presented. A part of present article is dedicated to a number of developed in recent years projects for large overhead crossings over water obstacles, where new generation conductors are used– these are high-temperature high strength aluminum clad steel ACS conductors developed and manufactured by Lumpi-Berndorf (Austria). Furthermore, here original constructions of towers, tension and suspension clamps and foundations, which were developed to make possible to use higher mechanical strength of these conductors and provide the necessary reliability of other OHL elements are considered. It is shown that designing of large crossings using HTLS conductors and individual designed towers, foundations and fittings can reduce construction costs by 15-40 %.

KEYWORDS

Overhead Transmission Lines – Reliability – Transmitting capacity – Conductors – Design optimization

1. Main advantages of the new generation conductors

As a matter of fact the main requirements for new generation conductors [1] are:

- The highest possible conductivity;

- The highest possible mechanical strength;

- Low linear mass;

- Small temperature elongation;

- Resistance to aging and wind-induced phenomena.

For traditional ACSR conductors operation temperature usually does not exceed 90° C. It is known that prolonged operation of a conductor (usually more than 2 hours) carried out at this temperature leads to a process of recrystallization of aluminum, as a result, it loses its mechanical strength and the whole mechanical load applied to the conductor is carried by the steel core of this conductor.[5] [6] In design of new generation high-temperature conductors conductive layers are made of heat-resistant aluminum alloys (TAL, ZTAL etc.), which allows continuous operation at temperatures of 150° C or higher with respect of the type of wires alloy.

Conductive part of new generation conductors can either be made of several layers of round wires, or using technology of compacting the layers by plastic compression, or profiled wires can be used. Both two last provide high fulfill factor of conductive cross section, whereby the compacted conductor in comparison with conventional construction with same diameter has greater cross-sectional area of conductive part. When the cross section of conductive components is the same for compacted and conventional conductors, the first ones have substantially smaller diameter, which is typically accompanied by smooth surface, and as a consequence, reduced aerodynamic drag-force.

Galvanized steel, aluminum clad steel, different steel alloys or composite materials can be used as a material for the core wires of new generation conductors. A core made of composite materials can be represented as a solid rod of circular cross section or as several twisted into a strand rods made of multicomponent composite material, consisting of a matrix (polymer, metal, carbon, etc.) and reinforcing elements (carbon fiber, basalt fiber, glass fiber, whiskers crystals, fine particles, etc.) which provide necessary mechanical strength. Usually application of composite core in construction of new generation conductors (ACCC, ACCR) enhances mechanical strength of a conductor, decreases its weight and thermal coefficient of linear expansion, what allows, when using conductors of such design, to provide reduced sag comparing to ACSR.

2. Successful experience of implementation of new generation ACCR conductors in renovation of existing OHL in Russian Federation

For the first time a composite core conductor ACCR was applied in Russian Federation during reconstruction of 110 kV OHL “Ochakovo-Odintsovo” 1 and 2, in 2008 by Company MOESC (Moscow). Conductors of this type are well known all over the world [1], [2], because they are already being used for over 10 years and there are more than 70 new construction projects as well as renovations of existing lines, which are accomplished in North and South America, in Europe, Asia and Africa. ACCR conductor consists of outer conductive wires of Al-Zr alloy, which retain their mechanical properties when heated up to temperatures of 2100 C, and a composite core made of wires, which comprise high purity aluminum and longitudinal aluminum oxide fibers, which provide a material with significantly high strength. The advantages of the composite core are low weight and low coefficient of thermal expansion, approximately two times less than that of steel.

During renovation of 110 kV OHL “Ochakovo-Odintsovo” a 13.1 km long conductor ACSR 240/32 was replaced by the ACCR conductor 477-T16 Hawk, with 238 mm2 cross section. The transmitting capacity of the line has been increased by 98 %. The reconstruction was performed using existing towers. Due to low linear weight of the conductor and low coefficient of thermal expansion there was significant increase of reliability and safety of the reconstructed line provided, taking the fact that this line crosses city's districts with high population density. At temperatures above 0° C distances from replaced conductor ACSR 240/32 to the ground in the number of spans was significantly less than 6 m required by the standards, and that was creating certain risks for the population and for the network safety. After reconstruction safe distances to the ground are preserved in all operational conditions of the OHL.

A similar project of replacing an old conductor by an ACCR was implemented in the area Nagatino - Gardeners, Moscow, in the context of a planned reconstruction. The customer of the project was the company "Central Electrical Networks", branch of Network Company MOESC (Moscow). The work on the project was carried out in 2011. Planned reconstruction of OHL "Cheryuomushki - South" was carried out for the purpose of increasing transmitting capacity of line up to 1000 A due to increased power consumption of the area. The solution to this problem using standard methods would require an installation of an underground 110 kV cable line or construction of new towers for OHL 220 kV, which would cause a number of problems in the conditions of dense city construction of Moscow and loaded road infrastructure. Application of ACCR allowed to use existing towers and increase transmitting capacity to desired values with a fair margin without a need for costly and large-scale construction work. ACCR conductor has low weight, it is 10-15 % lighter than ACSR conductor of same diameter, and can be easily installed on old towers. This prolongs the life of existing structures, solves the problem of incorrect distances from conductor to the ground and the problem of often clearings due to excess of allowed transmitted power in peak load conditions.

Totally there were successfully implemented seven such projects based on the application of ACCR in Russia: in addition to two mentioned above projects in Moscow the project in the Chita region, executed during renovation of OHL 110 kV Kharanorskaya GRES - substation Urga; in Irkutsk during renovation of OHL 110 kV Irkutsk Hydroelectric power station- Yuzhnaya- Kirovskaya; in Perm [3] during renovation of OHL 110 kV TEC 9 - TEC 6 and Perm - TES 6; during renovation of the network infrastructure, providing new capacity output unit of Vologda Thermal power plant; during renovation of the network object in Kuzbass. In all these cases, line capacity was increased by 50 % - 98 %. Due to a significant increase of distances from conductors to the ground and to different obstacles in the zone of safety along OHL, reliability and availability of the reconstructed elements of network infrastructure are significantly improved.

3. Successful experience of application of new generation gap type conductors GTACSR

In 2009, in short terms there was an important for South department of FSC UES of Russia project of reconstruction of 220 kV single-circuit OHL "Afipskaya - Crimean", for the purpose of increasing its transmitting capacity executed. Technically, reconstruction was to replace old conductor ACSR 300/56 on the entire length of the line, which is 73 km. As a result of feasibility study a high-temperature gap-type conductor GTACSR 217/49 was selected. Compared with ACSR 300/56, this conductor has a higher transmitting capacity and improved mechanical characteristics, including reduced diameter and weight.

The smaller diameter and weight, together with the feature of conductor’s construction, which provides only a slight sag increase when heated, made possible to reduce loads on the towers. It provided an opportunity to use the old towers with few reinforcements, despite of the fact that their life time was almost 50 years already. Due to lower sag and a possibility to heat conductor up to 1500 C during special events, the maximum transmitting capacity of OHL was increased by approximately 40%. According to experience of exploitation during last 4 years after the reconstruction, there were no accidents at this OHL, associated with conductor operation. In contradiction to the other experiences, there have not been a TV/Radio interference and audible noise near the line corridor discovered. As a result of the reconstruction, which provided a considerable decrease in the number of OHL shutdowns, the reliability of power supply at Southwestern district of Krasnodar region, which includes a large and socially important resort area, significantly increased.

4. Various types of Russian design new generation conductors and their application on the territory of the Russian Federation

Successful examples of the application of HTLS conductors led to internal Russian developments of new generation conductors of different types. There is a series of currently developed high temperature steel-aluminum conductors of AST and ASk2u types. AST conductors consist of galvanized steel wires in the core and aluminum heat-resistant Al-Zr alloy wires, which are stranded into concentric layers upon the steel core. For compacted conductors ASk2u aluminum wires of trapezoidal shape are used, and conductor’s core consists of a high-strength steel wires with Zn-Al protective coating. Application of high tensile steel wires allows to increase the mechanical strength of conductor and thereby reduce the sag while reconstructing existing OHL, reduce the risks of conductor’s breakage due to natural catastrophic events. Application of ASk2u conductors in construction of new OHL potentially reduces the number of intermediate towers by means of increasing the distances between them. The conductors ASk2u are applied on three 35-110 kV OHL in power utility "Kirovenergo", and also on OHL 500 kV Don Nuclear Power Station - Borino (Eletskaya).

Nowadays in Russia there are also developed HTLS conductors similar to well-known ACCC conductors, and which have found application in a number of network companies. The main material of the composite core (Figure 1a) – is high strength carbon fiber and epoxy binder of hot curing. To protect the carbon fiber parts of the composite core from metal conductive part of the conductor and from the phenomenon of galvanic corrosion an external non-conductive (insulating) shell - fiberglass on the basis of unidirectional glass fibers was used. A current carrying component of the conductor consists of profiled trapezoidal wires (Fig. 1b) and has a fill factor close to 0.95. A high temperature  aluminum alloy ZTAL is used as a material of this component.

| Composite core (a) | Conductor sample(b) |
| --- | --- |
| Fig. 1. HTLS conductor of ACCC type |

5. Test results of HTLS conductor developed in Russia

Series of tests were carried out to determine Russian HTLS compacted conductor’s mechanical and electrical parameters taking into account the recommendations of IEC 60794-4-1, IEC 61395, IEC 62004 and ASTM E831:

- Definition of parameters of construction;

- Determination  of strength and deformation of the conductive wires of the conductor before and after heated up to temperature of 150° C and cooled afterwards;

- The tensile tests to determine:

- modulus of elasticity of the composite core;

- modulus of elasticity of conductive alloy;

- modulus of elasticity of conductor;

- stress at 1% elongation of the core;

- tensile strength of the composite core.

- Stretching tests to determine:

  - creep deformation of the conductor under the influence of constant load of 45% of the tensile strength for 1,000 hours;

  - end modulus of elasticity (stretching).

- Determination of coefficient of thermal elongation of the composite core;

- Determination of coefficient of thermal elongation of the conductor;

- Determination of electrical resistance of the conductor to constant current at temperatures (20 ÷ 150)° C;

- Testing the “conductor - suspension clamp" system for resistance to the effects of 100 million cycles of oscillations of Aeolian vibration.

- Testing the “conductor - suspension clamp" system for resistance to the effects of 100 thousand cycles of oscillations in galloping mode.

- Determination of mechanical tensile strength (Fig. 2) (strength of conductor fixing  in the system):

- «conductor – tension clamp»;

- «conductor -  connecting clamp»;

- Determination of electrical contact quality of the "conductor-clamp" system after thermal aging (500 cycles of heating - cooling).

- Determination of limit current loads, taking into account solar radiation, ambient temperature, wind speed and direction on the conditions, that mechanical strength of conductors will be retained and the preservation of the smallest allowed vertical distance from conductors to the ground and / or intersected objects will be provided.

Specially designed line fittings: tension, connecting and suspension clamps were used during the tests.

The results obtained for 24.7 mm diameter Russian HTLS compacted conductor (with high-strength carbon-composite core diameter of 9.1 mm, conductive part cross-section 400 mm2) compared with the ACSR 400/64 are given in Table 1.

Table 1. The results of comparative tests of ACSR 400/64 and HTLS conductors

| Characteristic of the conductor | ACSR 400/64 | HTLS | Result of comparison of main characteristics, % |
| --- | --- | --- | --- |
|  | value | value |  |
| Cross section of conductive part, mm2 | 390 | 390,4 | +0,1% |
| Cross section of the core, mm2 | 64 | 65 | +1,5% |
| Diamiter of conductor, mm | 27,7 | 24,7 | –10,8% |
| Mechanical tensile strength, N | 129183 | 170233 | +31,8% |
| Weight of 1 km of conductor, kg | 1572 | 1204 | –23,4% |
| Maximum current load at the allowed temperature, A: 70 ° C2. 90 ° C3. 150 ° C4. | 860 1053 - | 1090 1310 1802 | +26,7% +24,4% +71,1%5 |
| Span length at the same sag of conductor, m | 350 | 435 | +11,5% |
| Number of towers at 5 km of OHL | 16 | 13 | –18,7% |
| Temperature coefficient of linear expansion of the core, 10-6 1/°С | 12 | 1,95 | –83,7% |
| Temperature coefficient of linear expansion of conductor, 10-6 1/°С | 19,2 | 17,2 | –10,4% |
| Sag at ambient temperature -5 ° C in III wind and ice region in different lengths of span, m: 350 400 450 | 8,92 11,72 14,84 | 5,74 7,51 9,50 | –35,9% |
| Losses on remagnetization at the economic current density, % from major thermal losses | 5,1 | none | – |
| Initial electric field intensity on the surface of conductors corresponding to emergence of a general corona effect in conditions of fair weather, Е0, kV/cm | 31,73 | 37,3 | +17,6% |

1 Percentage of increasing/decreasing of values of parameters in comparison with ACSR 400/64 conductor

2 at the ambient temperature 250C and wind speed 1 m/s

3 long-term allowed temperature of conductor

4 maximum long-term allowed temperature of HTLS conductor

5 in relation to maximum current load of ACSR 400/64 conductor at 900C

Fig. 2. HTLS conductor mounted with tension clamps at test facility

The results of the test showed that in comparison with conventional ACSR conductor of the same conductive part cross-section the Russian HTLS conductor have the following advantages:

- Reduction of the outer diameter of the conductor ~10 %;

- Reduction of weight  ~ 19.5% ;

- Increase of the tensile strength  ~ 40 % ;

- Reduction of the coefficient of linear expansion  ~ 15 % ;

- Increase of the length of the span at the same sag ~ 11.5% ;

- Reduction of the number of intermediate supports on 10 km line length ~ 14 % ;

- Increase of the maximum current load (increasing of capacity) ~ 71%.

Trial operation and comparison of technical and economic indices of the newly developed HTLS conductor will allow to reveal all its advantages comparing with traditional ACSR conductors deeply.

6. Application of new generation conductors on large crossings over water obstacles

In recent years a number of projects with large overhead crossings over water obstacles was developed. There were new generation conductors – high temperature ACS conductors with increased tensile strength used.

In order to use higher mechanical strength of these conductors, higher strength of other respective elements of the line is required: towers, tension and suspension clamps. Specially developed towers and high-load tension clamp, allow to use advantages of new conductors to the maximum, which leads to economic benefits from their application.

6.1 OHL crossing 220 kV “Perm GRES- Soboly” across Kama reservoir

6.1.1 Conductors, ground wires and towers

For the first time a high temperature high strength conductor was applied in 2009 for the design of a double circuit 220 kV crossing Perm GRES - Soboly OHL across Kama reservoir with total length of 2080 meters.  At the design stage of basic technical solutions two variants of the crossing were considered [4] (Fig. 3).

The first – to use conventional steel-aluminum conductor ACSR 500/336. In given climatic conditions (II wind area, III ice area) as an optimal crossing scheme was chosen T-A-A-T scheme (T-terminal, A-anchor) with the use of transitional tubular towers of individual development AT 133 and terminal towers K330 -2 5 K. The height of the AT 133 tower is 154 m, the height of suspension of the lower conductor - 133 m . An OPGW and C300 ground wire were considered.

The second - to use a high-temperature high-strength conductor. Specially for the conditions of this crossing a ACS 521-A20SA conductor was designed, and that made possible to use the T–S–S-T scheme of the crossing (T-terminal, S-suspension) with towers PP330-2/79,5 made of angle car and flats, both with terminal towers K330-2+5K. The height of tower PP330-2/79 5 was 104.4 m, height of suspension of the lower conductor - 75.2 m. For ground wires there were OPGW Stalum 510 2C and a ACS 521 -A20SA as a conventional ground wire used.

Data for comparative analysis of the two options considered are shown in Table 2, the crossing schemes for both variants are shown in Figure 3.

Figure 3. Schemes of the OHL 220 kV crossing “Perm GRES – Soboly”-1, 2across the Kama Reservoir, when applying ACSR 500/336 conductor (red) and ACS 521-A20SA conductor (blue).

Table 2. Technical data of the OHL 220 kV crossing across the Kama Reservoir

| Parameter | Conductors |
| --- | --- |
|  | ACSR | HTLS conductor |
| Conductor type | ACSR 500/336 | TACSR/ACS 521-A20SA |
| Conductor diameter, mm | 37.5 | 29.7 |
| Conductor sag, m | 145.6 | 86 |
| Conductor length on crossing, m | 6 x 2123.7 | 6 x 2096 |
| Conductor weight on crossing, ton | 51.03 | 44.2 |
| Cost per 1 ton of conductor, USD/ton | 4 781 | 7 750 |
| Code of tower | AT133(AT155-22) | PP300-2/79.5K |
| Height of lowest cross arm, m | 133 | 79.5 |
| Total height of tower | 154 | 106 |
| Weight of tower, ton | 410 | 154.4 |

6.1.2 Construction of foundations and installation of towers for the big overhead crossing across the Kama reservoir

Solid-cast reinforced concrete foundations of an individual production were developed to install the towers of the crossing (Fig. 4). Solid-cast foundations of similar construction are used for installation of towers on the left and right banks of the Kama reservoir, four under each crossing tower and two under each end tower. Each foundation is a solid-cast reinforced concrete column three-stage construction, outer dimensions of foundation for a crossing tower are 7.2 m x 7.2 m x 4.8 m. In preparation of foundation pit for a gravel layer on the high bank a non-woven geo-textile material is used, it is laid on the soil – soft ductile loam – to prevent washing out of the gravel.

During construction of the crossing, in 2010, the towers were mounted by building-up scheme (Fig. 5), (Fig. 6).

Figure 4. Solid-cast renforced concrete foundation used for mounting of a tower of the overhead line 220 kV crossing Permskaya GRES - Soboli-1,2 across the Kama reservoir.

Figure 5. Mounting of a tower of the overhead line 220 kV crossing Permskaya GRES - Soboli-1,2 across the Kama reservoir.

Figure 6. Tower PP330-2/79,5K on the right Bank of the Kama reservoir crossing.

6.1.3 Fittings

A new anchoring helical dead-end fitting has been developed for attachment of conductors and ground wires to the towers (Fig. 7). This dead-end consists of two load-bearing helical strands with mutually opposite winding directions. Load-carrying strands are mounted on a core either directly on one another or onto the pre-assembled armor rods and then by means of standard fittings are attached to the tower. The design of load-carrying strands of the clamp are designed in such a way that arising torsion moments compensate each other when strands are loaded. Maximum allowed load for this dead-ends is 800 kN.

Figure 7. Tension helical dead-end clamp with two load-strands installed on the terminal tower

6.1.4 The economic effect achieved

The following results are obtained from calculation of budget cost of constructing of the OHL 220 kV crossing across the Kama Reservoir: when ACSR conductor is used the budget cost of construction in the prices of 2009 is 6.02 million USD, and when a high-temperature conductor is used it is 4.98 million USD.

The optimization of structure units due to application of a high-temperature conductor allowed to reduce height of the crossing tower by 50 meters, to reduce its weight from 410 to 155 tons and to reduce the budget cost of the construction by 17% in comparison with if the ACSR conductor has been applied.

6.2 Other big crossings

In 2009 there were transitional towers made of pipes and foundations for them which consist of boring piles with metal grillages and a bulk filled muff developed for the OHL 220 kV crossing “Pechora GRES – Ukhta – Mikuns” across the Pechora River. An application of a high-temperature conductor ACS 548-A20SA allowed to reduce height of towers from 115 to 78 meters and to reduce the weight of each tower of OHL crossing from 186 to 135 tons. This led to a reduction of budget cost of construction by 15% in comparison with if an ACSR conductor of traditional design has been applied.

In 2011 an application of a high-temperature conductor ACS 521-A20SA allowed to reduce the height of transitional towers from 165 to 125 m, the budget cost of construction was reduced by 14% on OHL “Balakovo” 1,2 crossing across the Volga River with four single-circuit  and one double-circuit. Combined steel reinforced concrete foundations produced from precast elements of factory production and foundations consisting of boring piles with a monolithic grillage were developed for various soil conditions on the right and left coasts of the Volga River and on the island Pustinny.

In 2012 an application of a high-temperature TACSR/ACS 146-TAL/519-A20SA conductor allowed to reduce height of transitional towers from 220 to 180 m for a big OHL 500 kV crossing “Sovetsko-Sosninskaya-Parabel” across the Ob River. The developed towers were mounted in swampy conditions by using monolith reinforced concrete foundations with installation of an inter foundation crossbar made of pipes and providing protection against an ice drift.

7. Conclusions

During construction of new and renovation of existing OHL application of new generation conductors with improved mechanical and electrical characteristics, if compare with ACSR conductors of traditional design, application of special tension, connecting and suspension fittings helps to increase transmitting capacity and reliability of power supply and reduce investments per 1 MW of power transmitted.

Application of new generation conductors on big crossings taking optimization of tower design and foundations into account allows to reduce significantly the cost of construction of a crossing: by 15-40% due to reduction of material amount needed for towers and foundation, and also reduction of labor expenses for their production and installation.

BIBLIOGRAPHY

[1] 	Working Group B2.26 CIGRE. “Guide for qualifying high temperature conductors for use on overhead transmission lines” (Technical Brochure nr 426, August 2010).

[2]	R.Kotov “Electric Power: two jubilees” (Trends, Fvents, Markets. Federal business jornal, №5, May 2012).

[3]	A.Pravkov “Future -  for new technologies” (Electrical energy, № 1, January-February 2013).

[4]	R.C.R. de Mendez, J.D. Riera, L.F.F. Miguel, J. Kaminski Jr, L.F.F. Miguel, J.B.G. Ferreira da Silva “On Modeling the Dynamic Response of the 190m-high Tower for the Crossing of Trombetas River in the Amazon Region” (CIGRE Session 2012, B2-212).

[5]    CIGRE TB 244 CONDUCTORS FOR THE UPRATING OF OVERHEAD LINES

[6]    CIGRE Guide to Operation of Conventional Conductor Systems above 100 C

# Text boxes

21, rue d’Artois, F-75008 PARIS 	B2 _ 205 _2014	CIGRE 2014

http : //www.cigre.org